GIDDINGS & LEWISâ

PiC Application Note

Document Number:  AN000018

Topic:  Drive Fuse Sizing

Scope

This PiC Application Note applies to all Giddings & Lewis Centurionä drives (DSM100, DS100, DS200, and AS100) and motors (SSM, FSM, and HSM).

Purpose

This application note provides information on the sizing of the fuses for use with Giddings & Lewis Centurion Servo Drives.  The approach taken is conservative.  In many cases a smaller fuse may be selected if performance requirements are known and guaranteed not to change.

Fuse Sizing Method

To size a fuse the power output (kW) of each axis must be known.  This can be derived by calculating the horsepower for each axis and converting that horsepower into units of watts.

Pout=KW=SpeedRPM∗(Torquelb−in)HP63,025∗746WattsHP∗KW1,000Watts

Pin=Pout∗ 2

Iin=PinVACin(RMS)        Single Phase Power

Iin(RMS per phase)=Pin3VACin(RMS)        Three Phase Power

Note: The factor of 2.0 is used to account for the power factor and losses of the system.

If you are using the Systex sizing program, the average speed and average torque data has been calculated and can be used in the above equation.

Example

You are using DS130 drive and SSM460 motor, and you are not sure of the exact speed and torque in your application.  Look at the speed/torque curves for the selected drive/motor combination as shown in the Centurion section of the Product Guide.  Select the values for the worst case continuous speed and torque.  The SSM460 with a DS130 is capable of 4,000 RPM and a torque of 40 lb-in.

Note: The speed/torque curves are based upon a drive module input voltage of 230 VAC. For a 115 VAC input voltage, the maximum speed is reduced by half.

Pout=KW=4000RPM∗(40lb−in)HP63,025∗746WattsHP∗KW1,000Watts=1.89KW

Pin=1.89KW∗ 2  =3.8KW

Iin=3.8KW230VAC(RMS) =16.5 Amps        Single Phase Power

You should select a fuse with a minimum rating of 17 Amps.

Slow blow fuses are required to allow for in rush current during power initialization at the power terminals.  Time delay versions of UL Class J, Class R , or equivalent fuses are acceptable, local regulations must be observed.

Revision History

Date:  02/21/96

Author:  Jeff Johnson

Changes:  Original

Date:  [For each revision, enter the date revised,]

Author:  [the name of the person revising the document,]

Changes:  [and indicate what changes were made.]